**Section 654.403 Recommended Finished Water Contaminant Concentrations**

It is recommended that concentrations of constituents listed in Table A not be exceeded in the finished water.

|  |
| --- |
| Table A - SECONDARY MAXIMUM CONTAMINANT LEVELSFOR FINISHED WATER |
| Contaminant | Reported As | Levelmg/l\* |
| Chloride | Cl | 250. |
| Color | Color Units | 15. C.U. |
| Copper | Cu | 1. |
| Foaming Agents | MBAS | 0.5 |
| Hydrogen Sulfide | H2S | 0.05 |
| Iron | Fe | 0.3 |
| Manganese | Mn | 0.05 |
| Odor | Threshold Odor Number | 3. T.O.N. |
| Sulfate | SO4 | 250. |
| Total Dissolved Solids | TDS | 500. |
| Zinc | Zn | 5. |

\* Unless otherwise indicated.