**Section 350.TABLE E Construction Types and Sprinkler Requirements for New Intermediate Care Facilities for the Developmentally Disabled of Sixteen (16) Beds or Less**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Construction Type | | | | Stories | |
| 1 | 2 |
|  | | | |  |  |
| 2-hour Protected Noncombustible | | | | X | X |
| 1-hour Protected Noncombustible | | | | X | X\* |
| Noncombustible | | | | X\* | X\* |
| Heavy Timber | | | | X\* | X\* |
| 1-hour Protected Ordinary | | | | X\* | X\* |
| 1-hour Protected Wood Frame | | | | X\* | X\* |
| Ordinary | | | | X\* |  |
| Frame | | | | X\* |  |
|  | | | |  |  |
|  | | | |  |  |
| Key: | X | = | Allowed types of construction | | |
|  | \* | = | Building requires automatic fire extinguishment protection | | |

(Source: Amended at 15 Ill. Reg. 466, effective January 1, 1991)