**Section 860.TABLE B Water Distribution Pipe Size**

|  |  |  |
| --- | --- | --- |
| Inside Diameter of Main (In inches) | Number of Manufactured Home Sites Connected | Maximum Length of Main (In feet) |
|  |  |  |
| 2 | 20 | 600 |
| 3 | 60 | 1,800 |
| 4 | 120 | 3,600 |
| 6 | 400 | 12,000 |

NOTE: If local requirements exceed the above sizes, the local standards must be met. A minimum 6-inch diameter pipe is required if fire hydrants are installed in the water distribution system. (See Section 860.270(d).)

(Source: Amended at 30 Ill. Reg. 13419, effective July 28, 2006)