**Section 890.APPENDIX A**  **Plumbing Materials, Equipment, Use Restrictions and Applicable Standards**

**Section 890.TABLE H**  **Horizontal Fixture Branches and Stacks**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Maximum Number of Drainage Fixture Units (D.F.U.)  That May be Connected to: | | | |
|  |  |  | More than 3 Stories in Height | |
| Diameter of Pipe (inches) | Any Horizontal Fixture Branch | One Stack of 3 Stories in Height or 3 Intervals | Total for Stack | Total at One Story or Branch Interval |
| 1¼ | 1 | 2 | 2 | 1 |
| 1½ | 3 | 4 | 8 | 2 |
| 2 | 6 | 10 | 24 | 6 |
| 2½ | 12 | 20 | 42 | 9 |
| 3 | 201 | 302 | 602 | 161 |
| 4 | 100 | 240 | 500 | 90 |
| 5 | 360 | 540 | 1,100 | 200 |
| 6 | 620 | 960 | 1,900 | 350 |
| 8 | 1,400 | 2,200 | 3,600 | 600 |
| 10 | 2,500 | 3,800 | 5,600 | 1,500 |
| 12 | 3,900 | 6,000 | 8,400 | 1,500 |
| 15 | 7,000 | − | − | − |
| 1 Not over two water closets. | | | | |
| 2 Not over six water closets, or more than two per branch interval or per floor. | | | | |